## Sheet1
1. Power
| discharge | Q | 0.25 | [m³/s]
| gross head | H | 0.8 | [m]
| hydraulic efficiency | ηh | 0.9 | [-]
| water density | ρ | 999 | [kg/m³]
| acceleration of gravity | g | 9.81 | [m/s²]
| Power | P | 1764.0342 | [W]
2. Specific speed / rotational speed
| net head = (H x ηh) | Hn | 0.72 | [m]
| rational speed of the turbine RPM | n | 400 | [minˉ¹]
| specific speed (in minˉ¹) | nq | 255.8766 | [-]
| rational speed of the turbine | n | 6.6667 | [sˉ¹]
| specific hydraulic energy of machine = (Hn x g) | E | 7.0632 | [J/kg]
| specific speed (in sˉ¹) | nQE | 0.76936 | [-]
3. Runner diameter section
| runner diameter | De | 0.36254 | [m]
| hub diameter | Di | 0.13545 | [m]
5. Cavitation
| conical draft tube lenght!!!!! | L | 0.6 | [m/s]
| angle from axis to wall | x | 7 | [°]
| outlet velocity | c4 | 1.2244 | [m/s]
| atmospheric pressure | Patm | 94190 | [Pa]
| water vapor pressure | Pv | 1072.9 | [Pa]
| water density | ρ | 999 | [kg/m³]
| acceleration of gravity | g | 9.81 | [m/s²]
| net head = (H x ηh) | Hn | 0.72 | [m]
| specific speed----nQE | nQE | 0.76936 | [-]
For example, at 34 °C the pressure is 5.3240 kPa and at 102°C is 108.87 kPa.
| cavitation coefficient | σ | 1.1455 | [-]
| maximum allowed suction head | Hs(max) | 8.7532 | [m]
6. Design of the blade
6.1 Distortion of the blade under ideal circumstances
| rational speed of the turbine | n | 6.6667 | [sˉ¹] |  | 6=De | 5 | 4 | 3 | 2 | 1=Di
| net head = (H x ηh) | Hn | 0.72 | [m] | d | 0.36254 | 0.31712 | 0.2717 | 0.22628 | 0.18087 | 0.13545 | [m]
| acceleration of gravity | g | 9.81 | [m/s²] | u | 7.593 | 6.6417 | 5.6905 | 4.7393 | 3.788 | 2.8368 | [m/s]
| atmospheric pressure | Patm | 94190 | [Pa] | cu1 | 0.83979 | 0.96006 | 1.1205 | 1.3455 | 1.6833 | 2.2478 | [m/s]
| area betven hub in De | A∞ | 0.088819 | [m²] | cu2 | 0.90439 | 1.0339 | 1.2067 | 1.449 | 1.8128 | 2.4207 | [m/s]
| velocity after runner | c3 | 2.4218 | [m/s] | wu1 | -6.7532 | -5.6817 | -4.57 | -3.3938 | -2.1047 | -0.58904 | [m/s]
|  | H1 | 0.65 | [m] | wu2 | -6.6886 | -5.6078 | -4.4838 | -3.2903 | -1.9752 | -0.41613 | [m/s]
|  | H2 | 0.7 | [m] | wu∞ | -6.7209 | -5.6448 | -4.5269 | -3.3421 | -2.04 | -0.50259 | [m/s]
| suction head | Hs | 0.1 | [m] | wm | 2.8147 | 2.8147 | 2.8147 | 2.8147 | 2.8147 | 2.8147 | [m/s]
| efficiency of the energy change (0.88 to 0.91) | ηs | 0.88 | [-] | w1 | 7.3163 | 6.3407 | 5.3672 | 4.4092 | 3.5146 | 2.8757 | [m/s]
| profile characteristic number (2.6 to 3) | K | 2.6 | [-] | w2 | 7.2567 | 6.2746 | 5.294 | 4.33 | 3.4386 | 2.8453 | [m/s]
| minimal water pressure (2 to 2.5) | pmin/γ | 2 |  | w∞ | 7.2865 | 6.3076 | 5.3306 | 4.3694 | 3.4762 | 2.8592 | [m/s]
| specific weight of water | γ | 9804 | [N/m³ | β∞ | 157.276 | 153.4972 | 148.1274 | 139.8956 | 125.9329 | 100.1239 | [°]
| Angle of slip | λ | 3 | [°] | (180-β∞) | 22.724 | 26.5028 | 31.8726 | 40.1044 | 54.0671 | 79.8761 | [°]
6.2 Lift and drag cofficient |  |  |  |  | ζa | 1.036 | 1.3827 | 1.9364 | 2.883 | 4.5575 | 6.7451
[5 empty] | sin(180-β∞-λ) | 0.33749 | 0.39879 | 0.48286 | 0.60327 | 0.77788 | 0.97388
| hydraulic efficiency | ηh | 0.9 | [-] | cos(λ) | 0.99863 | 0.99863 | 0.99863 | 0.99863 | 0.99863 | 0.99863
ζa | gross head | H | 0.8 | [m] | 1/t | 0.14085 | 0.13625 | 0.13131 | 0.12616 | 0.12234 | 0.13032
[5 empty] | t/l | 7.0998 | 7.3394 | 7.6153 | 7.9263 | 8.1739 | 7.6734
ρψωφςεβαμηζ